## Slide 1: PATAREI as a building and a structure
Roode Liias
Professor, Tallinn University of Technology

## Slide 2
limestone
    compressive strength starting with 200 kg/cm2
    frost resistance 15
  limestone of higher quality
    compressive strength starting from 600 kg/cm2
    frost resistance more than 25
limestone is considered as national stone

## Slide 4
patarei as a fully deserted building today
  no proper use, no proper user
  normal wear and tear
  years with no maintenance
  several re-building cases
  traces of vandalism
  process of obsolesence

## Slide 5
technical condition of Patarei
  major survey has been done in 2005
  in today’s presentation
    general description of the situation
    no exact locations for the defects are highlighted

## Slide 6
structural issues
  limestone structures have preserved their major qualities
  fully deteriorated roof

## Slide 7
dampness and moisture
  the greatest danger for any building
  flow of moisture from the ground
  influence of rain ja snow
  high humidity degree in the rooms
Aspergillus
Penicillium
Stachybotrys
Cladosporium

## Slide 8
roofs
  fully damaged
  steel sheets have weared out
  timber frame structures are fully rotten

## Slide 9
walls
  carbonising process and salts have settled
  thermal bridges around the windows
  plaster in the rooms is mostly damaged
  danger of diseases in some buildings and rooms

## Slide 10
ground water and foundations
  foundations are not damaged
  there is no insulation to protect the structures from the flow of moisture
  vertical insulation would not help much
limestone
granite
clay
level of ground water

## Slide 11
problems with ground floor-rooms
  very high constant humidity level
  no ventilation
  all vertical wells for heating and ventilation are bricked up
  massive mould nets

## Slide 12
roode.liias@ttu.ee
thank you